| Title | Apply and remove earths from conductors on electricity supply networks |  |  |
| --- | --- | --- | --- |
| Level | 4 | Credits | 4 |

| Purpose | People credited with this unit standard are able to: demonstrate knowledge of earthing and bonding requirements for conductors on electricity supply networks; prepare to apply earths to conductors in electricity supply networks of all voltages; prove earthing point de-energised; apply and remove the earths from conductors on the electricity supply network; and report work done on applying and removing earths from electrical conductors, plant and equipment. |
| --- | --- |

| Classification | Electricity Supply > Electricity Supply - Distribution Networks |
| --- | --- |

| Available grade | Achieved |
| --- | --- |

Guidance Information

1	Evidence presented for assessment against this unit standard must be consistent with safe working practices and be in accordance with applicable legislative and industry requirements.

2	Legislation, regulations and/or industry standards relevant to this unit standard include but are not limited to:

- Electricity Act 1992

- Electricity (Safety) Regulations 2010

- Health and Safety at Work Act 2015

- NZECP 35:1993 New Zealand Electrical Code of Practice for Power Systems Earthing available at https://www.worksafe.govt.nz/

- Electricity supply industry codes of practice and documented enterprise procedures, including Safety Manual – Electricity Industry (SM-EI) and relevant EEA guides available at www.eea.co.nz

and any subsequent amendments and replacements.

3	Definitions

Asset owner refers to a participant who owns or operates assets used for generating or conveying electricity.

Industry requirements include all asset owner requirements; manufacturers’ specifications; and enterprise requirements which cover the documented workplace policies, procedures, specifications, business, and quality management requirements relevant to the workplace in which assessment is carried out.

4	Assessment of practical skills against the outcomes in this standard requires three practical observations from three different workplace activities.

5	Earths include multi-phase and single-phase earths.

Outcomes and performance criteria

Outcome 1

Demonstrate knowledge of earthing and bonding requirements for conductors on electricity supply networks.

Range	Electricity (Safety) Regulations 2010, SM-EI, EEA Guide to Work on De-energized Distribution Overhead Lines, NZECP 35.

Performance criteria

1.1	Requirements for earthing for safe working are described.

1.2	Responsibilities of employees when applying earths to overhead line conductors or underground cables are described.

1.3	Statutory and enterprise inspections and care of insulating sticks and voltage detection devices are demonstrated in terms of manufacturers’ specifications and recommendations.

1.4	Requirements of earthing for operation of protective equipment are described.

1.5	Equipotential zones in the workplace are described.

1.6	The causes of step and touch voltages in the workplace are described.

1.7	Bonding of conductors, equipment and plant to create an equipotential work zone is described.

Outcome 2

Prepare to apply earths to conductors in electricity supply networks of all voltages.

Range	overhead electric lines or underground cables.

Performance criteria

2.1	Conductors are physically identified.

Range	single line diagram, labels, line, plant and equipment layout.

2.2	Inspection confirms or assures that the conductors to be earthed have been isolated in accordance with industry standards.

Range	Electricity Safety Regulations 2010, SM-EI, EEA Guide to Work on De-energized Distribution Overhead Lines.

2.3	Earth attachment positions on conductors and the local earth are identified.

Range	industry standards, earthing terminals, tail clamp attachment points, clamp rating and compatibility.

2.4	Procedures and requirements for portable earths are determined.

Range	issuer instructed, recipient applied.

2.5	Earthing equipment is inspected for compliance.

Range	compliance – satisfactory for use, surface condition and cleanliness;

equipment – clamps, leads, fittings, sticks and poles, terminations.

Outcome 3

Prove earthing point de-energised.

Range	includes but is not limited to – voltage detection device, proving unit, insulation stick.

Performance criteria

3.1	Circumstances when use of voltage detection device is required are identified.

Range	overhead or underground conductors, first earth, out of sight of other applied earths, integral earthing not possible, capacitor.

3.2	Voltage detection device and insulating stick for network system voltage are selected.

3.3	Voltage detection device is tested before and after use to ensure serviceable condition is maintained.

Range	audible test, visual test.

3.4	Earthing points are proven de-energised on overhead or underground cable.

Range	voltage detection device or spiking tool.

Outcome 4

Apply and remove the earths from conductors on the electricity supply network.

Performance criteria

4.1	Personal protective equipment is worn and used in accordance with SM-EI.

Range	includes but is not limited to – hard hats, appropriate gloves, overalls, footwear.

4.2	Approvals are obtained.

Range	access permit, operating order, teams warned off permit area.

4.3	Earths are applied.

Range	tail clamp connection to earth first, leads kept away from person, positive connection made and held in place before clamping, bonding across any conductor to be broken or equipment to be opened, bonding to adjacent metal, equipotential environment for work.

4.4	Earths are removed.

Range	issuer instructed, recipient applied.

4.5	Access permit is returned.

Range	issuer instructed, recipient applied.

Outcome 5

Report work done on applying and removing earths from electrical conductors, plant and equipment.

Range	may include but is not limited to – operating order, recipient safety measure form.

Performance criteria

5.1	Reported information is complete, concise, and legible.

5.2	Information is recorded in the required format and filed in the correct location.

| Planned review date | 31 December 2027 |
| --- | --- |

Status information and last date for assessment for superseded versions

| Process | Version | Date | Last Date for Assessment |
| --- | --- | --- | --- |
| Registration | 1 | 19 August 1997 | 31 December 2016 |
| Review | 2 | 27 April 2001 | 31 December 2016 |
| Review | 3 | 22 October 2003 | 31 December 2016 |
| Rollover and Revision | 4 | 20 June 2008 | 31 December 2016 |
| Review | 5 | 21 July 2011 | 31 December 2016 |
| Review | 6 | 20 March 2014 | 31 December 2020 |
| Review | 7 | 28 September 2017 | 31 December 2020 |
| Revision | 8 | 28 June 2018 | 31 December 2024 |
| Review | 9 | 2 March 2023 | N/A |

| Consent and Moderation Requirements (CMR) reference | 0120 |
| --- | --- |

This CMR can be accessed at http://www.nzqa.govt.nz/framework/search/index.do.

Comments on this unit standard

Please contact Waihanga Ara Rau Construction and Infrastructure Workforce Development Council at qualifications@WaihangaAraRau.nz if you wish to suggest changes to the content of this unit standard.