| Title | Terminate high voltage polymeric insulated power cables up to 33kV in the electricity supply industry |  |  |
| --- | --- | --- | --- |
| Level | 4 | Credits | 10 |

| Purpose | People credited with this unit standard are able to terminate high voltage polymeric insulated cables up to 33kV in the electricity supply industry. |
| --- | --- |

| Classification | Electricity Supply > Electricity Supply - Distribution Networks |
| --- | --- |

| Available grade | Achieved |
| --- | --- |

| Prerequisites | Unit 20061, Terminate high voltage polymeric insulated power cables up to 22kV in the electricity supply industry, or demonstrate equivalent knowledge and skills. |
| --- | --- |

Guidance Information

1	Evidence presented for assessment against this unit standard must be consistent with safe working practices and be in accordance with applicable legislative and industry requirements.

2	Legislation, regulations and/or industry standards relevant to this unit standard include but are not limited to the current version of the Health and Safety at Work Act 2015; Electricity Act 1992; Electricity (Safety) Regulations 2010; and any subsequent amendments and replacements; Electricity supply industry codes of practice and documented enterprise procedures, including Safety Manual – Electricity Industry (SM-EI) (2015) available at www.eea.co.nz.

3	Definitions

Asset owner refers to a participant who owns or operates assets used for generating or conveying electricity.

HV is defined as ‘high voltage’ and includes voltages exceeding 1000V AC.

Industry requirements include all asset owner requirements; manufacturers’ specifications; and enterprise requirements which may include the documented workplace policies, procedures, specifications, business, and quality management requirements relevant to the workplace in which assessment is carried out.

4	This unit standard excludes tough plastic sheath (TPS) type cables.

Outcomes and performance criteria

Outcome 1

Terminate high voltage polymeric insulated cables up to 33kV in the electricity supply industry.

Performance criteria

  - Work site is prepared, and a safe working zone is established.

Range	includes – scope of work, identification and testing of cables, tools and equipment.

1.2	Terminations are prepared.

Range	cleaning, conductor preparation, stripping, earthing, moisture management, positioning.

1.3	Conductors are terminated.

Range	may include but is not limited to – compression, mechanical, weld, shearbolt, cleanliness, moisture management;

evidence of three is required.

1.4	Conductors are re-insulated.

Range	may include but is not limited to – barrier, elastomer, heat shrink, tapes, resins, void filling, screens, cable core separation;

evidence of four is required.

1.5	Mechanical and environmental integrity and earth continuity are re-established.

1.6	Cables are tested after termination.

Range	includes but is not limited to – visual, HV pressure testing, insulation resistance, continuity test, sheath integrity, phase testing to manufacturers’ specifications.

1.7	Termination as built is recorded to asset owner’s requirements.

| Planned review date | 31 December 2025 |
| --- | --- |

Status information and last date for assessment for superseded versions

| Process | Version | Date | Last Date for Assessment |
| --- | --- | --- | --- |
| Registration | 1 | 22 October 2003 | 31 December 2016 |
| Review | 2 | 21 August 2009 | 31 December 2016 |
| Review | 3 | 18 September 2014 | 31 December 2022 |
| Review | 4 | 27 February 2020 | 31 December 2022 |
| Review | 5 | 27 August 2020 | N/A |

| Consent and Moderation Requirements (CMR) reference | 0120 |
| --- | --- |

This CMR can be accessed at http://www.nzqa.govt.nz/framework/search/index.do.

Comments on this unit standard

Please contact Connexis - Infrastructure Industry Training Organisation qualifications@connexis.org.nz if you wish to suggest changes to the content of this unit standard.