| Title | Maintain control valve actuators and positioners |  |  |
| --- | --- | --- | --- |
| Level | 3 | Credits | 5 |

| Purpose | People credited with this unit standard are able to: – stroke-check control valve actuators and calibrate positioners; and – service control valve actuators and positioners. |
| --- | --- |

| Classification | Industrial Measurement and Control > Industrial Measurement and Control - Maintenance |
| --- | --- |

| Available grade | Achieved |
| --- | --- |

Guidance Information

1	This unit standard has been developed for learning and assessment in a workplace environment.

2	For control valves or self actuating values refer to Unit 2639, Maintain and service control valves in accordance with industry requirements.

3	References

ANSI/ISA-51.1-1979 (R1993) Process Instrumentation Terminology;

Electricity Act 1992;

Electricity (Safety) Regulations 2010;

Health and Safety at Work Act 2015 and associated regulations;

ISSN 0114-0663, New Zealand Electrical Codes of Practice, available from Worksafe, https://worksafe.govt.nz/;

and all subsequent amendments and replacements.

4	Definitions

Industry requirements – includes all asset owner requirements, manufacturers’ specifications; and enterprise requirements which cover the documented workplace policies, procedures, specifications, business requirements; and quality management requirements relevant to the workplace in which the assessment is carried out.

Service – planned activity during normal operation that involves inspection, cleaning, testing, adjusting or making minor repairs to a piece of equipment to ensure that it works properly.

5	Recommended skills and knowledge: Unit 2638, Demonstrate knowledge of control valves, actuators, and positioners.

Outcomes and performance criteria

Outcome 1

Stroke-check control valve actuators and calibrate positioners.

Range	two control valve actuators, two control valve positioners.

Performance criteria

1.1	Identify hazards in terms of inherent risk.

Range	may include but is not limited to – stored energy (springs), moving parts, compressed air.

1.2	Explain and follow safe work procedures.

Range	may include but is not limited to – isolations applied, process media drained, trapped-pressure released.

1.3	Select test equipment according to required accuracy and range of devices.

Range	may include but is not limited to – pneumatic test-set including regulated air-signal sources and test gauges, DC signal source.

1.4	Identify type and cause of typical errors.

Range	may include but is not limited to – packing friction, stem wear, lost motion, weak springs, diaphragm failure, pneumatic leaks, incorrect air supply pressure, incorrect calibration, lost data.

1.5	Calibrate devices as specified by the data sheet.

Range	may include but is not limited to – specified air-supply pressure, actuator stroke, actuator bench set, positioner zero, span and characteristic.

1.6	Document test results in accordance with industry requirements.

Outcome 2

Service control valve actuators and positioners.

Performance criteria

# 2.1	Identify hazards in terms of inherent risk.

Range	may include but is not limited to – stored energy (springs), moving parts, compressed air.

2.2	Explain and follow safe work procedures.

Range	may include but is not limited to – isolations applied, process media drained, trapped-pressure released.

2.3	Locate, interpret, and apply technical information for servicing equipment.

2.4	Identify types and causes of damage to control valve actuators and positioners.

Range	may include but is not limited to – operating environment, vibration, air quality, valve-action, diaphragm failure, stem wear, incorrect set-up and adjustment.

2.5	Service actuators to ensure continued operation.

Range	tools, materials, parts, techniques, specifications;

actuator types – diaphragm, single acting piston, double acting piston, electric, hydraulic, electro-hydraulic;

evidence of two different types is required.

2.6	Service positioners to ensure continued operation.

Range	tools, materials, parts, techniques, specifications;

positioner types – 4-20mA, pneumatic, force balance, motion balance, electro-pneumatic, digital, electro-hydraulic;

evidence of two different types is required.

2.7	Produce reports and documentation in accordance with industry practice.

This unit standard is expiring.  Assessment against the standard must take place by the last date for assessment set out below.

Status information and last date for assessment for superseded versions

| Process | Version | Date | Last Date for Assessment |
| --- | --- | --- | --- |
| Registration | 1 | 31 October 1995 | 31 December 2013 |
| Revision | 2 | 30 October 1997 | 31 December 2013 |
| Revision | 3 | 3 April 2001 | 31 December 2013 |
| Review | 4 | 22 June 2001 | 31 December 2013 |
| Review | 5 | 19 May 2008 | 31 December 2019 |
| Review | 6 | 21 November 2013 | 31 December 2027 |
| Rollover and Revision | 7 | 28 June 2018 | 31 December 2027 |
| Review | 8 | 30 January 2025 | 31 December 2027 |

| Consent and Moderation Requirements (CMR) reference | 0003 |
| --- | --- |

This CMR can be accessed at http://www.nzqa.govt.nz/framework/search/index.do.